## Slide 1
DRAFT REGULATION FOR PUBLIC COMMENT • CENTRAL ELECTRICITY AUTHORITY
CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment Regulations, 2026
Mandatory grid-forming inverters and co-located energy storage for renewable energy plants
23 Dec 2022
Principal Regulations
Original Technical Standards notified
03 Sep 2026
Draft 2nd Amendment
Published for public comment
04 Oct 2026
Comments Due
To Chief Engineer (Legal), CEA
Issued under Section 177, Electricity Act 2003 • F.No. CEA-TH-17/1/2021-TETD Division • Gazette of India, Extraordinary, Part III—Section 4
WHY IT
MATTERS
This is a short, sharply-targeted amendment — just one new sub-regulation — but it directly changes the economics of every solar and wind project commissioning after mid-2027.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 1

## Slide 2
At a Glance
Core facts on the draft amendment
ISSUING AUTHORITY
Central Electricity Authority (CEA), under Section 177(2)(e), Electricity Act 2003.
WHAT IT AMENDS
Inserts new sub-regulation 106B(20) after 106B(19) of the 2022 Technical Standards Regulations.
CORE REQUIREMENT
Grid-forming control on inverters/BESS PCS, plus co-located storage for new solar & wind plants.
WHO MUST COMPLY
Solar & wind IPPs, BESS developers, inverter/PCS OEMs — for plants commissioned after 1 Jul 2027.
COMMENT WINDOW
30 days from public availability of the Gazette notification — CEA has set 04.10.2026 as the deadline.
HOW TO COMMENT
By post to Chief Engineer (Legal), CEA, or e-mail to celegal-cea@gov.in.
WHY IT
MATTERS
The comment deadline is fixed — 04.10.2026 — not a rolling window, so drafting and sending comments early leaves room to follow up if CEA seeks clarification.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 2

## Slide 3
What's Changing
New Regulation 106B(20) — inserted after 106B(19)
A single new sub-regulation, in three parts
1
Grid-forming control
≥15% of inverter capacity + all BESS PCS on new RE plants must have grid-forming control, per the CEA Connectivity Standards.
2
Co-located storage — Phase 1
Ground-mounted solar & onshore wind commissioned after 1 Jul 2027 need an ESS ≥ 2-hour duration, sized at 10% of plant capacity.
3
Co-located storage — Phase 2
For plants commissioned 1 Jul 2029–30 Jun 2031, the ESS duration requirement steps up to ≥ 4 hours, same 10% capacity sizing.
WHY IT
MATTERS
The amendment doesn't replace anything existing — it only adds 106B(20). Everything else in the 2022 Technical Standards Regulations stays exactly as it was.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 3

## Slide 4
Applicability Timeline
Two commissioning-date thresholds set the requirement
1 Jul 2027
Grid-forming control + ESS (2-hr, 10%) becomes mandatory for new RE plants
1 Jul 2029
ESS duration requirement steps up to 4 hours (still 10% capacity)
30 Jun 2031
End of the 4-hour window — any further change to be notified separately
Both thresholds are keyed to COMMISSIONING date, not the date a PPA is signed or construction begins — a plant that breaks ground before 1 Jul 2027 but commissions after it is still covered.
WHY IT
MATTERS
Projects currently in construction with a commissioning date anywhere near mid-2027 should check this timeline first — a few months' slippage can flip which regime applies.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 4

## Slide 5
Requirement 1: Grid-Forming Control
Inverters and battery PCS
The rule
At least 15% of inverter capacity on a renewable energy power plant commissioned after 1 Jul 2027 must have grid-forming control. All PCS (Power Conversion System) units of any battery energy storage system on such a plant must also have grid-forming control. Compliance is measured against the technical requirements already specified in the CEA (Technical Standards for Connectivity to the Grid) Regulations.
Why grid-forming, not grid-following
• Grid-following inverters need a stable grid frequency/voltage reference to synchronise — they can't hold up a weak grid on their own. • Grid-forming inverters can set their own voltage/frequency reference, giving inertia-like support as coal capacity's share of generation falls. • As RE penetration rises, more grid-forming capacity is what keeps frequency stable during faults and sudden generation loss.
WHY IT
MATTERS
This effectively creates a new technical spec line item for inverter and BESS PCS procurement — developers should confirm OEM roadmaps for grid-forming-capable equipment now, not at commissioning.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 5

## Slide 6
Requirement 2: Co-Located Storage — Phase 1
Applies to plants commissioned 1 Jul 2027 onward
Ground-mounted Solar Power Plants and on-shore Wind Power Plants
2 hrs
MINIMUM STORAGE DURATION
The ESS must be able to discharge continuously for at least 2 hours.
10%
MINIMUM STORAGE CAPACITY
Sized against the plant's installed capacity (MW), not its ESS energy rating.
Co-located
SITING REQUIREMENT
The ESS must be physically co-located with the generating plant, not remote.
Worked example (as given in the draft): A 100 MW solar plant commissioned after 1 Jul 2027 needs a minimum of 10 MW of co-located storage, able to discharge for 2 hours.
WHY IT
MATTERS
Note what's exempt: rooftop solar, floating solar, and off-shore wind are not named in this sub-regulation — only ground-mounted solar and on-shore wind carry the storage mandate.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 6

## Slide 7
Requirement 2: Co-Located Storage — Phase 2
The duration requirement steps up for 2029–2031 vintage plants
Commissioning window
Storage duration
Storage capacity
100 MW plant needs
1 Jul 2027 – 30 Jun 2029
2 hours
10% of capacity
10 MW for 2 hours
1 Jul 2029 – 30 Jun 2031
4 hours
10% of capacity
10 MW for 4 hours
What stays constant vs. what changes
✓ Capacity sizing (10% of plant MW) is identical across both windows. ✓ The siting requirement (co-located, ground-mounted solar / on-shore wind only) doesn't change. → Only the discharge duration doubles — from 2 hours to 4 hours — for the 2029–2031 vintage. ⚠ Any future change to these percentages or durations will be separately notified by CEA — this isn't necessarily the final word.
WHY IT
MATTERS
For a project that might slip from 2029 into 2029–2031 timing, the storage bill roughly doubles in duration terms — worth flagging in financial models now, before it becomes a surprise at financial close.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 7

## Slide 8
Who Is Affected — and How
Six stakeholder groups with distinct exposure to this amendment
Solar & Wind IPPs / Developers
Directly — bear the capex for storage + grid-forming inverters on every new project after 1 Jul 2027.
BESS Developers & System Integrators
New demand for co-located storage sized to this rule, but also new PCS grid-forming spec to meet.
Inverter / PCS Manufacturers
Must have grid-forming-capable products certified and available well before mid-2027.
Discoms / Distribution Licensees
Benefit from more grid-stable RE supply, but may see PPA tariffs rise to reflect added capex.
Industry / Trade Associations
Represent aggregate sector concerns — timelines, cost pass-through, standardisation.
General Public / Consumers
Ultimate bill-payers if added compliance costs flow through tariffs — also benefit from grid reliability.
WHY IT
MATTERS
Each of these six groups has a genuinely different stake — a one-size comment letter reads as generic to CEA; a stakeholder-specific letter reads as informed engagement.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 8

## Slide 9
How to Submit Your Comments
Deadline: 04 October 2026
04.10.2026
Latest date for comments to reach CEA — by post or e-mail. Comments received after this date may not be considered.
By post
Chief Engineer (Legal)
Sewa Bhawan (North Wing), Room No. 622, 6th Floor
R.K. Puram, New Delhi – 110066
By e-mail
celegal-cea@gov.in
Cite F.No. CEA-TH-17/1/2021-TETD Division in the subject line.
What to include
Your name/organisation · stakeholder category · specific clause referenced (Reg. 106B(20)) · the change sought and why.
WHY IT
MATTERS
A comment that cites the exact sub-regulation number and proposes specific replacement wording is far more likely to be taken up than one that objects in general terms.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 9

## Slide 10
Prepared for stakeholder comment-drafting
A short amendment with an outsized impact on RE + storage economics from mid-2027 onward.
Practical note: this deck is a reference and comment-drafting aid, not a substitute for the Gazette notification or a legal opinion. Verify the operative text against the official CEA publication before finalising any submission.
WHY IT
MATTERS
The window to influence the final wording closes 04 Oct 2026 — after that, whatever CEA notifies becomes binding on every qualifying project.
Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, 2026
Slide 10