Draft CEA (Technical Standards for Construction of Electric Plants and Electric Lines) 2nd Amendment, Regulations, 2026

Comments due 04.10.2026   |   Notified 03 Sep 2026   |   Amends the 2022 Technical Standards Regulations   |   1 new sub-regulation: 106B(20)

| ISSUING AUTHORITY & BASIS Central Electricity Authority, under Section 177(2)(e) of the Electricity Act, 2003. Published in the Gazette of India, Extraordinary, Part III, Section 4. | WHAT IT AMENDS Inserts a new sub-regulation 106B(20) after 106B(19) of the CEA (Technical Standards for Construction of Electric Plants and Electric Lines) Regulations, 2022 (notified 23.12.2022). No other clause is touched. |
| --- | --- |

| REQUIREMENT 1 — GRID-FORMING CONTROL At least 15% of inverter capacity on a renewable energy plant commissioned after 1 Jul 2027 must have grid-forming control. All PCS units of any co-located BESS must also have grid-forming control, per the CEA Connectivity Standards. | REQUIREMENT 2 — CO-LOCATED STORAGE Ground-mounted solar & on-shore wind plants commissioned after 1 Jul 2027 must have a co-located ESS of at least 2-hour duration, sized at 10% of installed capacity. Rooftop/floating solar and off-shore wind are not covered. |
| --- | --- |

| STORAGE DURATION STEP-UP For plants commissioned 1 Jul 2029 – 30 Jun 2031, the required ESS discharge duration rises from 2 hours to 4 hours. Capacity sizing (10% of plant MW) stays the same in both windows. | WORKED EXAMPLE A 100 MW ground-mounted solar plant commissioned after 1 Jul 2027 needs ≥ 10 MW of co-located storage able to discharge for 2 hours; if commissioned in the 2029–31 window, the same 10 MW must discharge for 4 hours. |
| --- | --- |

| WHO IS AFFECTED Solar & wind IPPs/developers, BESS developers & integrators, inverter/PCS OEMs (directly); Discoms, industry associations and consumers (indirectly, via tariffs and grid reliability). | FUTURE CHANGES The draft explicitly reserves CEA's right to notify any change to the grid-forming percentage or ESS capacity requirement “from time to time” — this is not necessarily the final calibration. |
| --- | --- |

HOW TO SUBMIT COMMENTS — BY 04.10.2026

•  By post: Chief Engineer (Legal), Sewa Bhawan (North Wing), Room No. 622, 6th Floor, R.K. Puram, New Delhi – 110066.

•  By e-mail: celegal-cea@gov.in — cite F.No. CEA-TH-17/1/2021-TETD Division in the subject line.

•  Reference the exact clause (Regulation 106B(20)) and propose specific wording where seeking a change, rather than objecting in general terms.