Draft CERC (Indian Electricity Grid Code) (Second Amendment) Regulations, 2026

Comments due 21.10.2026   |   Draft dt 21.09.2026   |   Effective on Gazette publication; Para 16(B) from 01.04.2027

| TRIAL RUN & INFIRM POWER (REGS 19, 21, 22, 25A) Trial-run notice 7→3 days. Solar/wind/ESS ≥250 MW may test in ≥50 MW instalments (no limit); standalone ESS min 50 MW, 50–250 MW balance in ≤3 instalments of ≥5 MW. RLDC may grant multiple infirm-power extensions up to 3 months cumulative (request ≥10 days ahead). Infirm power scheduled only after trial-run certificate; 7-day right of first offer to contracted buyers if PPA is silent. | PUMPED STORAGE & COD (REGS 22(3)(F),(J), 24, 27) PSP trial run per unit; >4 h cumulative interruption = repeat; low reservoir lets COD proceed, with later demonstration or de-rating from COD. COD of last unit = plant COD. Grid-Code COD delinked from PPA pre-conditions. Transmission-constrained plants: rated capacity within 1 yr of GNA effectiveness or COD, whichever later. |
| --- | --- |

| CONGESTION CHARGE (NEW REG 30A) Levied on regional entities aggravating flow above TTC (warning at ATC; ≥2 clear blocks notice; withdrawn at ATC with 1 block notice). In addition to DSM. Wheeling regions with both corridors congested: any deviation charged. Weekly RPC statement; pay in 10 days; 0.04%/day interest. 2009 Congestion Regulations repealed; old rate/procedure continue till replaced. | THERMAL USD, SCUC & PEAK DC (REGS 45–47, ANNEX-9) USD intimation 14:30 D-1; beneficiaries retain units by 15:30 (≥50% MCR); USD declaration 16:00; final list 16:30; MTL top-up 17:00; final USD 18:00. Capacity charge continues on off-bar DC; failure to revive on schedule ≥ MTL = forced outage. NLDC may decommit any time. Peak-hour DC may not be below off-peak DC. |
| --- | --- |

| DEFAULTING ENTITIES (NEW REG 45(16)) Default trigger date: 75 days after RPC account, or next working day after PSM lapse. Then T-GNA (incl. exchanges) cut entirely; after 2 more months GNA short-term cut; long-term access cut 5% per month. Restored within 1 day of payment. (RLDC Fees Regs use 1 month / 10%.) | FREE POWER & RESERVES (REG 45(17), ANNEX-8, REG 30(11)) State Govts may sell free-power share at CHGS bus bar under one RLDC Standing Clearance; in DSM pool at Normal Rate; no transmission charges/losses. Reserves estimated quarter-ahead for regional and state control areas; regional-entity bulk consumers share reserve obligations; ESS/PSP added to primary response. |
| --- | --- |

| RTM GATE CLOSURE (REGS 48–49, PARA 16) Phase-1 (to 31.03.2027): session 23:00–23:15 for 00:00 block; revision from 6th/7th block. Phase-2 (from 01.04.2027): 23:15–23:20 bidding, clearing to 23:30; revision from 5th/6th block. Final schedules 23:45 in both. | OTHER CHANGES RPC may revise declared hydro high-inflow period. Alternate-source supply by non-Sec 62 stations needs buyer's express (standing) consent. Reactive energy interest from due date. New definitions: CHGS, congestion charge, default trigger date, REIA. |
| --- | --- |

HOW TO COMMENT

•  Email secy@cercind.gov.in and shilpa@cercind.gov.in on or before 21.10.2026; registered users may upload via SAUDAMINI (e-Regulation link).

•  Helpdesk: 011-20904365 Ext. 260 / 7042604928. Late comments may not be considered.

•  Ready-to-adapt comments letter, DIY worksheet and Comments Deck: powerppt.com → Submit Comments.