## Slide 1
COMMENTS • READY TO ADAPT AND SEND
Comments & Clarification Queries
on the Draft List of Relevant Standards
Under CEA (Measures relating to Safety and Electric Supply) Regulations, 2023 — Ref. CEA-PS-16/6/2026-CEI Division-Part(1)
10
Points Drafted
Ready to send
15.11.26
Deadline
Send well before this
CEI
Named Contact
Chief Engineer (CEI), CEA
WHY IT
MATTERS
These are genuine clarificatory points a prospective commenter would raise — three directly echo “(To check IS)” flags CEA left in its own draft. Review and adapt before sending.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 1

## Slide 2
How to Use This Deck
Turning these points into an actual submission
1. Review
Read through each point and mark which ones are genuinely relevant to your organisation's position.
2. Adapt
Edit the wording to reflect your specific facts — generic points land better when clearly grounded in a real case.
3. Consolidate
Combine selected points into a single letter/email using the covering-letter template in the companion DOCX.
4. Send early
Submit well before 15.11.2026 — leave time for a reply or for CEA to actually consider it.
WHY IT
MATTERS
Keep points specific and reference CEA-PS-16/6/2026-CEI Division-Part(1) by name for the fastest, most credible response.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 2

## Slide 3
Points 1–2
Reference points for the covering letter/email
1
No standard listed at all
S.No. 33 — Reg. 99 (Plans)
This row carries no Relevant Standard entry, though the clause requires plans to be reviewed “as per the relevant standards.” Please specify the applicable standard or confirm none applies.
2
Gas-area clause cites IEC only, no IS
S.No. 36 — Reg. 112 (Precautions where gas exists)
Only IEC 60079 parts are listed under International Standard, with no Indian Standard, though BIS has adopted most of these as IS/IEC 60079 parts. Please add the IS/IEC equivalents.
WHY IT
MATTERS
A statutory inspection plan with no standard to cite is effectively unenforceable on paper — worth flagging before the final gazette locks it in.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 3

## Slide 4
Points 3–4
Reference points for the covering letter/email
3
Row left entirely blank
S.No. 53
This numbered row is entirely blank — no regulation reference and no standard. Please complete it or remove it from the published list.
4
“Hand lines” left unmapped
S.No. 4 — Reg. 21(2) (marked “To check IS” by CEA)
Seven IS standards are listed for PPE and tools, but none for “hand lines,” which the regulation names explicitly. Please add the applicable standard or confirm the omission is intentional.
WHY IT
MATTERS
A missing row number is a visible sign something didn't make it into the final compilation — cheap to catch now, awkward after gazetting.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 4

## Slide 5
Points 5–6
Reference points for the covering letter/email
5
FRLS/HFFR cable edition unclear
S.No. 12 — Reg. 38(3)(iv) (marked “To check IS” by CEA)
IS 694 and IS 17048 are cited for fire-retardant cables used above fifteen metres. As IS 694 has multiple revised parts, please confirm the specific part/edition intended.
6
Transformer fire-system citation flagged
S.No. 21 — Reg. 46(2)(ix) (marked “To check IS” by CEA)
IS 15325 and IS 15519 are cited for automatic fire-fighting systems on transformers of 10 MVA+ — both cover water-spray/water-mist specifically. Please confirm these are intended, or clarify if other technologies are also acceptable.
WHY IT
MATTERS
Multiple IS 694 editions exist; an ambiguous citation in a safety-critical fire-rated cable clause is exactly the kind of gap that causes disputes later.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 5

## Slide 6
Points 7–8
Reference points for the covering letter/email
7
Garbled regulation name
S.No. 28 — Reg. 70(2)
The Regulation Name column reads “(Communication lines lighetning prote)” — apparently truncated and misspelled. Please correct this text in the published version.
8
Drafters' own scope question left open
S.No. 31 — Reg. 77 (Protection against lightning)
This row carries CEA's own bracketed note “(it covers all installations?)”. Please resolve this and state explicitly whether Reg. 77 applies uniformly across overhead lines, substations and generating stations.
WHY IT
MATTERS
A cosmetic fix, but a published Gazette-linked reference list with visible text corruption looks unfinished — an easy, free credibility win for CEA.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 6

## Slide 7
Points 9–10
Reference points for the covering letter/email
9
Regulation figure vs. standard may conflict
S.No. 32 — Reg. 79 (marked “to check the depth in IS” by CEA)
The regulation specifies a minimum depth of 1.2 metre for cables above 33 kV, while cited IS 1255 specifies depth by voltage class. Please confirm the 1.2 metre figure is consistent with IS 1255.
10
BESS clauses lean almost entirely on foreign standards
S.No. 54–65 — Regs. 122(B)–122(K), Battery Energy Storage Systems
Most BESS sub-clauses cite UL 1973, UL 9540, UL 9540A, NFPA 855, NFPA 90A/90B, NFPA 101, IEEE 693/1547/1578 and ASTM B117, with only IS 17067, IS 17092 and IS 3043 appearing across the whole section. Please list the IS 17067-series equivalent as the primary reference wherever BIS has published one.
WHY IT
MATTERS
A numeric figure in the regulation and a cross-referenced standard that may say something different is exactly the kind of silent conflict that causes site-level compliance disputes.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Slide 7

## Slide 8
10 points, one deadline — 15.11.2026
Send the points that matter to your position — not all of them need to apply.
Practical note: these are draft points compiled from the source notification and draft List of Relevant Standards. They are not a substitute for the official text or legal/consulting advice. Select and adapt only what's relevant before sending.
WHY IT
MATTERS
Companion documents: the done-for-you covering letter + table (DOCX), and the DIY drafting worksheet — use this deck to walk a team through the points before finalising either.
Draft List of Relevant Standards (CEA Safety & Electric Supply Regs.) — Comments
Last slide